## Room Schedule
room_number | room_name | room_function | cleanliness_class | pressure_target | zone_id | supply_air (m3/h) | return_air (m3/h) | fresh_air (m3/h) | exhaust_air (m3/h) | return_terminal | return_terminal_qty | exhaust_terminal | exhaust_terminal_qty | filter_qty | filter_spec | balance_error (m3/h) | validation
101 | Open Office | office | non-clean | 0 | AHU-1 | 1200 | 900 | 300 | 0 | T3 | 2 | — | 0 | 0 |  | 0 | OK
102 | Meeting Room | office | non-clean | 0 | AHU-1 | 400 | 280 | 120 | 0 | T2 | 1 | — | 0 | 0 |  | 0 | OK
103 | Reception | corridor | non-clean | 0 | AHU-1 | 250 | 190 | 60 | 0 | T1 | 2 | — | 0 | 0 |  | 0 | OK
104 | Toilet Block | toilet | non-clean | - | AHU-1 | 180 | 0 | 180 | 220 | — | 0 | T2 | 1 | 0 |  | -220 | air balance off by -220.0 m3/h (supply=180, return=0, fresh=180, exhaust=220)
105 | Kitchen | kitchen | non-clean | - | AHU-1 | 300 | 0 | 300 | 450 | — | 0 | T2 | 2 | 0 |  | -450 | air balance off by -450.0 m3/h (supply=300, return=0, fresh=300, exhaust=450)
201 | Clean Lab | lab | ISO-7 | + | AHU-2 | 2050 | 1600 | 400 | 0 | T3 | 3 | — | 0 | 4 |  | 50 | air balance off by +50.0 m3/h (supply=2050, return=1600, fresh=400, exhaust=0)
202 | Prep Room | lab | ISO-7 | + | AHU-2 | 850 | 640 | 160 | 0 | T3 | 1 | — | 0 | 2 |  | 50 | air balance off by +50.0 m3/h (supply=850, return=640, fresh=160, exhaust=0)
203 | Gowning | changing | ISO-8 | + | AHU-2 | 400 | 280 | 70 | 0 | T2 | 1 | — | 0 | 1 |  | 50 | air balance off by +50.0 m3/h (supply=400, return=280, fresh=70, exhaust=0)
204 | Transfer Airlock | transfer | ISO-8 | + | AHU-2 | 250 | 160 | 40 | 0 | T1 | 2 | — | 0 | 1 |  | 50 | air balance off by +50.0 m3/h (supply=250, return=160, fresh=40, exhaust=0)
301 | Server Room | IT | non-clean | + | AHU-3 | 3550 | 3400 | 100 | 0 | T3 | 5 | — | 0 | 0 |  | 50 | air balance off by +50.0 m3/h (supply=3550, return=3400, fresh=100, exhaust=0)
302 | Storage | storage | non-clean | 0 | AHU-3 | 150 | 120 | 30 | 0 | T1 | 1 | — | 0 | 0 |  | 0 | OK
303 | Corridor | corridor | non-clean | 0 | AHU-3 | 200 | 150 | 50 | 0 | T1 | 1 | — | 0 | 0 |  | 0 | OK

## Zone Summary
zone_id | room_count | total_supply (m3/h) | total_return (m3/h) | total_fresh (m3/h) | total_exhaust (m3/h) | filter_qty | terminal_T1 | terminal_T2 | terminal_T3
AHU-1 | 5 | 2330 | 1370 | 960 | 670 | 0 | 2 | 4 | 2
AHU-2 | 4 | 3550 | 2680 | 670 | 0 | 8 | 2 | 1 | 4
AHU-3 | 3 | 3900 | 3670 | 180 | 0 | 0 | 2 |  | 5